## Slide 1
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Dynamic Imaging Particle Analysis
Data Center Coolants

## Slide 2: Migration to Liquid Cooling
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
As computing power increases at an almost exponential rate, heavily driven by the increased adoption of AI and expansion of cloud computing, it has massively driven up equipment cooling requirements.
While traditional racks often operated at 5–10 kW, modern AI optimized racks now commonly require 40–60+ kW, and projections indicate that leading-edge, liquid-cooled racks will soon reach 100–600+ kW per rack.

## Slide 3: Migration to Liquid Cooling
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Historically common air cooling systems simply cannot handle such a heat load, which has accelerated the move towards liquid based cooling systems

## Slide 4: Current Industry Guidelines and Standards
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
The industry is moving quickly, and existing standards and guidelines are primarily written around air cooling systems, with large gaps related to liquid cooled systems
American Society of Heating Refrigerating and Air-Conditioning Engineers
TC 9.9 deals with Data Centre cooling
Members / contributors include global leading companies in IT software / hardware companies as well as cooling system hardware and coolant chemical manufacturers
Last document published in 2021
Updated version with heavy focus on liquid cooling expected in 2026-2027
Not a formal standards body, and is more a collaborative community working on an area of common interest
Similar membership profile as ASHRAE
Publish more regular recommendations or guidelines than ASHRAE

## Slide 5: Types of Liquid Cooling
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Direct to Chip
Immersion
Cold plate through which coolant flows in micro channels, is mounted onto the chip itself
Entire Rack is submerged in coolant

## Slide 6: Types of Liquid Cooling
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Technology Cooling System (TCS) loops, circulate liquid coolant between a Coolant Distribution Unit (CDU) and the Cold Plates or the Immersion Bath

## Slide 7: Coolant Properties
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
The properties of the coolant fluid are critical, in order to ensure maximum heat transfer from the rack. Multiple parameters of the fluid require analysis;
Ethylene Glycol or Propylene Glycol Concentration (water / glycol mix)
pH
Hardness
Sulfate Concentration
Chloride Concentration
Suspended Particulate Size and Concentration

## Slide 8: Particle Contamination Issues
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Specifically for Direct to Chip Cooling;
Clogging of Micro Channels: Given the small size (100 – 500 micron), even minor particulate matter can plug these channels, causing severe, localized hot spots on the chip, leading to thermal throttling or catastrophic failure.
Reduced Cooling Efficiency: Even before completely plugging a channel, as particles accumulate, they create insulating layers that reduce heat transfer efficiency. This forces cooling pumps to work harder and increases the overall thermal resistance of the system.

## Slide 9: Particle Contamination Issues
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Direct to Chip and Immersion Cooling Systems;
Accelerated Corrosion: Particle contamination, especially when combined with moisture, accelerates corrosion throughout the cooling loop. Corrosive byproducts can create sludge, leading to further clogging, or pit the cold plates, causing coolant leaks and premature failure of pumps and heat exchangers.
Abrasive Pump Wear: Impurities in the coolant act as abrasives that cause premature wear and failure of pumps and valves within the liquid cooling unit (CDU).

## Slide 10: Particle Contamination Sources
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Corrosion Byproducts
Metallic particles from pipes and connectors.
Manufacturing Residue
Leftover materials from the construction of the cooling hardware
Environmental Debris
Dust or other materials entering during maintenance
Biological Growth Bacteria or algae in the cooling fluid.

## Slide 11
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Target Application 1 – Particle Analysis on TCS Loops
Real time particle analysis on the TCS loop allows for;
Maintenance / replacement schedule planning on filtration equipment and the coolant itself
Instantaneous detection of any filter breakthrough or failure

## Slide 12
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Prior to delivery of TCS loop hardware (heat exchanger, tanks, piping, pumps etc.) the manufacturer must ensure the equipment is particle free.
The last manufacturing step is flushing the equipment with a cleaning fluid to remove suspended particles.
Monitoring the particle concentration in the flushing fluid discharge can determine when the equipment is particle free.
Target Application 2 – Particle Free TCS Hardware Supply

## Slide 13
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Basic principle of flowing the coolant fluid between a high intensity light source, and microscopic camera
The captured images are analysed in realtime by Cantyvision software, where they are measured under 40+ different size and shape parameters (major axis, minor axis, area, perimeter, circularity, aspect ratio….)
The Solution: Dynamic Imaging Particle Analysis

## Slide 14
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
LED Light Source
Gigabit Camera with Microscopic Lens
Flow Cell
Coolant In
The InFlow Analyser

## Slide 15
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Uncompressed GigE video combined with 4K lens for optimum image capture
Particle / Droplet Size to 1 - 295µm
Particle / Droplet Concentration: 0 – 2500 ppm(v) or 0 – 500,000 ppml
High Intensity (2000 Lumen) LED Light Source
50,000 Hours (5+ years) Continuous Use
Fused Glass Process Barrier;
- No dead space for particulate to be trapped
- No window gasket = ZERO chance of leaks
The InFlow Analyser

## Slide 16
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Uses CantyVision analysis software to process the live video feed from the InFlow, and provide detailed analysis of the suspended particulate size and concentration
Multiple outputs
Video Display
          4-20mA
        OPC
        MODBUS (TCP/IP or RTU)
Ease of Remote Support
Vector Control Module (VCM)

## Slide 17
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621

## Slide 18
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Analysis Interface 1 - Summary
PPM AND PPML DATA

## Slide 19
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Analysis Interface 2 – PPM Concentration

## Slide 20
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Analysis Interface 3 – ISO PPML Counts

## Slide 21
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Classification feature provides separate size / count / concentration outputs for each particle type present in the cooling fluid
Suspended Solids
Air Bubbles
Oil (Leak from Pumps)
Particle Classification

## Slide 22
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Visual differences in particle types are recognised due to the multi-dimensional size and shape measurement performed
Particle Classification

## Slide 23: Route to Market
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
TCS Cooling Loop Hardware Manufacturers
Data Centre Engineering
Design Companies
Coolant Chemical Manufacturers
Data Centre Operations Facilities Teams

## Slide 24: This concludes the Presentation!
JM Canty, Inc. · Buffalo, New York · Phone: (716) 625-4227 | JM Canty, Ltd. · Dublin, Ireland · Phone: +353 (1) 882-9621
Thanks for choosing CANTY!
For Further Information on this product please visit www.jmcanty.com.